## Sheet1
!!! Building Information
| Floor Number | 87
| Floor Height | 4.5
!Topology | Zone Number | 4
| Energy Station | 2
! Representive Floor | Representive Floor Number | 2
! Representive Floor 1 | Floor Range | 1 | 40
| Floor Load | C:\WD\Tong Ji University\TongJi University\(2014-06) Mega-tall Building\System\Components-20151209\Simulation Source Code\LoadR1.xlsx
! Representive Floor 2 | Floor Range | 41 | 87
| Floor Load | C:\WD\Tong Ji University\TongJi University\(2014-06) Mega-tall Building\System\Components-20151209\Simulation Source Code\LoadR2.xlsx
! Representive Floor 3 | Floor Range | 61 | 90
Floor Load
! Representive Floor 4 | Floor Range | 91 | 120
Floor Load
!Topology Option | Topology Option | 1 | 0
| Floor Equipment | 40
!!! Energy Station Information
!! Energy Station 1
! Chiller | Small Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 400
|  | Design COP | 5
|  | Number | 2
|  | Motor Efficiency | 0.95
| Middle Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 800
|  | Design COP | 5.2
|  | Number | 2
|  | Motor Efficiency | 0.95
| Large Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 1200
|  | Design COP | 5.5
|  | Number | 2
|  | Motor Efficiency | 0.95
! Primary Pump | Small Primary Pump | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  |  | a2 | 0.3998
|  |  | a3 | -0.1779
|  |  | a4 | 1.2704
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  |  | b2 | 0.0388
|  |  | b3 | 1.5378
|  |  | b4 | 0.0102
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  |  | c2 | -9.4625
|  | Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  |  | d2 | 1.283
|  |  | d3 | -1.42
|  |  | d4 | 0.5834
|  | Design Flow | 240
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
| Middle Primary Pump | Curve: Head versus Speed and Flowrate | a1
a2
a3
a4
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1
b2
b3
b4
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1
c2
|  | Curve:VFD Efficiency versus Speed | d1
d2
d3
d4
|  | Design Flow | 300
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
| Large Primary Pump | Curve: Head versus Speed and Flowrate | a1
a2
a3
a4
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1
b2
b3
b4
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1
c2
|  | Curve:VFD Efficiency versus Speed | d1
d2
d3
d4
|  | Design Flow | 300
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
! Secondary Pump AHU Zone 1 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
! Secondary Pump Heat Exchanger Zone 1 and 2 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
!Heat Exchanger 1 | Type | Counter Flow
| UA Parameter | m | 0.8
|  | n | 0.8
| Design Flow | 300
| Number | 2
! Secondary Pump AHU Zone 2 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
! Secondary Pump Heat Exchanger Zone 2 and 3 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
!Heat Exchanger 2 | Type
| UA Parameter | m | 0.8
n
| Design Flow | 300
| Number | 2
! Secondary Pump AHU Zone 3 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
!! Energy Station 2
! Chiller | Small Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 400
|  | Design COP | 5
|  | Number | 2
|  | Motor Efficiency | 0.95
| Middle Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 800
|  | Design COP | 5.2
|  | Number | 2
|  | Motor Efficiency | 0.95
| Large Chiller | CAPFT Coefficient | a1 | 0.2579
|  |  | a2 | 0.038902
|  |  | a3 | -0.00021708
|  |  | a4 | 0.046868
|  |  | a5 | -0.00094284
|  |  | a6 | -0.00034344
|  | EIRFT Coefficient | b1 | 0.93388
|  |  | b2 | -0.058212
|  |  | b3 | 0.0045004
|  |  | b4 | 0.00243
|  |  | b5 | 0.000486
|  |  | b6 | -0.001215
|  | EIRPLR Coefficient | c1 | 0.2229
|  |  | c2 | 0.31339
|  |  | c3 | 0.46371
|  |  | c4 | 0
|  | Design Capacity | 1200
|  | Design COP | 5.5
|  | Number | 2
|  | Motor Efficiency | 0.95
! Primary Pump | Small Primary Pump | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  |  | a2 | 0.3998
|  |  | a3 | -0.1779
|  |  | a4 | 1.2704
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  |  | b2 | 0.0388
|  |  | b3 | 1.5378
|  |  | b4 | 0.0102
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  |  | c2 | -9.4625
|  | Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  |  | d2 | 1.283
|  |  | d3 | -1.42
|  |  | d4 | 0.5834
|  | Design Flow | 240
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
| Middle Primary Pump | Curve: Head versus Speed and Flowrate | a1
a2
a3
a4
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1
b2
b3
b4
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1
c2
|  | Curve:VFD Efficiency versus Speed | d1
d2
d3
d4
|  | Design Flow | 480
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
| Large Primary Pump | Curve: Head versus Speed and Flowrate | a1
a2
a3
a4
|  | Curve:Wheel Efficiency versus Speed and Flowrate | b1
b2
b3
b4
|  | Curve: Motor Efficiency versus Speed and Flowrate | c1
c2
|  | Curve:VFD Efficiency versus Speed | d1
d2
d3
d4
|  | Design Flow | 720
|  | Design Head | 0.8
|  | Rated Speed | 6500
|  | Is VFD | Please Selected!
|  | Rated Efficiency | 0.8
! Secondary Pump AHU Zone 1 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
! Secondary Pump Heat Exchanger Zone 1 and 2 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
!Heat Exchanger 1 | Type | Counter Flow
| UA Parameter | m | 0.8
|  | n | 0.8
| Design Flow | 300
| Number | 2
! Secondary Pump AHU Zone 2 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 300
| Design Head | 2.5
| Rated Speed | 6500
| Number | 2
| Is VFD | Please Selected!
| Rated Efficiency | 0.8
! Secondary Pump Heat Exchanger Zone 2 and 3 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 200
| Design Head | 4
| Rated Speed | 3800
| Number | 5
| Is VFD | No
| Rated Efficiency | 0.8
!Heat Exchanger 2 | Type
| UA Parameter | m | 0.8
n
| Design Flow | 400
| Number | 2
! Secondary Pump AHU Zone 3 | Curve: Head versus Speed and Flowrate | a1 | -0.5121
|  | a2 | 0.3998
|  | a3 | -0.1779
|  | a4 | 1.2704
| Curve:Wheel Efficiency versus Speed and Flowrate | b1 | -0.6061
|  | b2 | 0.0388
|  | b3 | 1.5378
|  | b4 | 0.0102
| Curve: Motor Efficiency versus Speed and Flowrate | c1 | 0.9695
|  | c2 | -9.4625
| Curve:VFD Efficiency versus Speed | d1 | 0.5087
|  | d2 | 1.283
|  | d3 | -1.42
|  | d4 | 0.5834
| Design Flow | 200
| Design Head | 3
| Rated Speed | 3500
| Number | 2
| Is VFD | Yes
| Rated Efficiency | 0.8
! Cooling Tower Cell | Nominal Heat Transfer Rate | 432720
| Airside Flowrate | 13.89
| Waterside Flowrate | 0.021
| Rated Power | 5500
!!! Design Information
! HVAC system parameters | Outdoor Air Ratio | 20
| Chilled Water Temperature Difference | 5
| Condenser Water Temperature Difference | 5
| Heating Water Temperature Difference | 10
| AHU Air Side Outlet Temperature | 13
| Chilled Water Supplying Temperature | 5.5
| Condenser Water Returning Temperature | 30
| Heating Water Supplying Temperature | 60
| Design Water System Working Pressure | 2.5
! Outdoor Parameters | City selected | Shanghai
! Indoor Parameters | Dry Bulb Temperature | 25
| Relative Humidity | 55
!!!Simulation Control
!Time | Time Start | 2015 | 7 | 1
| Time End | 2015 | 11 | 1